## Slide 1: Simple but Complicated Air Quality Permitting for Generators

## Slide 2: Pinal County Generator Rules
Insignificant Units:
•Less than 325 HP (243 kW); and
•Operate less than 72 hours per year.
•Both the requirements have to be met in order to qualify for an exemption.
•Insignificant units are not permitted even if subjected to any of the federal
standards.
•More than one insignificant units at a source will be considered as one unit
and may need a permit.

## Slide 3: Federal Generator Rules
Reciprocating Internal Combustion Engine (RICE) National Emission Standard for Hazardous Air Pollutants (NESHAP)
  RICE NESHAP
  40 CFR Part 63 Subpart ZZZZ
  Generally pre-2006 engines of all fuel types
Stationary Compression Ignition (CI) Internal Combustion (IC) Engine New Source Performance Standard (NSPS)
  Compression Ignition NSPS
  40 CFR Part 60 Subpart IIII
  Generally post-2006 diesel engines
Stationary Spark Ignition (SI) Internal Combustion (IC) Engine New Source Performance Standard (NSPS)
  Spark Ignition NSPS
  40 CFR Part 60 Subpart JJJJ
  Generally post-2006 gas, natural gas and propane engines

## Slide 4: NESHAP and Emergency Generators at Area Sources
Example: 450 HP compression ignition diesel emergency generator, manufactured 5/1/2005, located at an area source of Hazardous Air Pollutants (HAPs)
  Area Source of HAPs = single HAP emissions less than 10 ton per year (tpy) and total HAP emissions less than 25 tpy
Engine Category = Emergency CI
Date Constructed = Before 6/12/06
Compliance Date = all compliance dates are in the past

## Slide 5: NESHAP and Emergency Generators Cont.
Emission Limitations, Management Practice and Other Requirements = CFR citations lead to Table 2d section labeled “ Requirements for Existing RICE Located at Area Sources”
  Change oil and filter every 500 hours or annually, whichever comes first
    Or follow oil analysis procedure
      Total Base Number is less than 30% of the Total Base Number of the oil when new
      Viscosity of the oil has changed by more than 20% from new
      Percent water content (by volume) is greater than 0.5
      If you meet all three you do not need to change the oil, if any fail you change the oil within 2 business days or before operation, whichever is later
  Inspect air cleaner every 1000 hours or annually, whichever comes first, and replace as necessary
  Inspect all hoses and belts every 500 hours or annually, whichever comes first, and replace as necessary

## Slide 6: NESHAP and Emergency Generators Cont.
Operating Limitations = No requirements
Fuel Requirements = Currently available low sulfur non-road (red dye) diesel
  Many facilities opt to use the currently available ultra low sulfur on-road diesel (available at gas stations)
  All the delayed compliance dates have passed
Performance Tests = No requirements

## Slide 7: NESHAP and Emergency Generators Cont.
Monitoring, Installation, Collection, Operation and Maintenance Requirements
  Follow the manufacturer’s maintenance plan and operate the engine in a manner consistent with good air pollution control practices
  Install a non-resettable hour meter
  Minimize time spent at idle during startup to less than 30 minutes
Initial Compliance = no requirements

## Slide 8: NESHAP and Emergency Generators Cont.
Continuous Compliance:
  No operational time limit on the use in emergency situations
  100 hours per calendar year limit for:
    Maintenance checks and readiness testing
    Emergency demand response (needs to be specifically addressed in your air quality permit)
    Periods where there is a deviation of voltage or frequency of 5% or greater below standard voltage or frequency
  50 hours per calendar year limit for non-emergency use
    Counts toward the 100 hour limit above
    Cannot be used for peak shaving or non-emergency demand response or to supply power to the grid (possible under certain conditions)

## Slide 9: NESHAP and Emergency Generators Cont.
Notification Requirements – No (Federal) requirements
  Check with your local Air Quality permitting agency to see if you need a permit.
Recordkeeping Requirements – Keep records of:
  Required maintenance
  Hours of operation (emergency vs. non-emergency)
Reporting Requirements:
  If greater than 100 HP and operates (or contractually obligated to be available) for more than 15 hours per calendar year for emergency demand response see 40 CFR 63.6650(h) for report requirements (includes electronic reporting to the USEPA)
  If maintenance is delayed due to the engine running during an emergency (or a few other reasons) report failures to change the oil (or due the analysis) and etc. on time

## Slide 10: NESHAP and Emergency Generators Cont.
NESHAP requirements are not applicable to the following:
  Existing residential emergency stationary RICE
    Homes or apartment buildings
  Existing commercial emergency stationary RICE
    Office buildings, hotels, stores, telecommunication facilities, restaurants, financial institutions, doctor’s offices, and sports and performing art facilities).
  Existing institutional emergency stationary Rice
  • Medical centers, nursing homes, research centers, correctional facilities, elementary and
  secondary schools, libraries, religious establishments, police stations, and fire stations

## Slide 11: NESHAP and Non-Emergency Generators at Area Sources
If under 300 HP and constructed before 6/12/06 similar to the emergency generator requirements.
If over 300 HP and constructed before 6/12/06
  Requires performance testing
  Carbon Monoxide emissions limited
    Generally requires add on controls (oxidation catalyst, CPMS or CEMS)
    Generally requires monitoring operational parameters
Testing can be avoided by retrofitting the pre-2006 engine with a post 2007 engine
Air Quality permit will likely set an annual operational limit.

## Slide 12: NSPS and Emergency Generators
Example: 450 HP Compression Ignition Emergency Generator, Manufactured 5/1/2015
Engines subject to an NSPS comply with the NESHAP by complying with the NSPS
Engine Category = 2007 model year and later emergency CI ICE < 30L/cyl displacement (except fire pump engines)
Date Constructed/Reconstructed/Manufactured = Commenced construction after 7/11/05 and manufactured after 4/1/06

## Slide 13: NSPS and Emergency Generators Cont.
Emission Standards:
  NMHC + Nox shall not exceed 4.0 g/kW-hr
  CO shall not exceed 3.5 g/kW-hr
  PM shall not exceed 0.20 g/kW-hr
  Exhaust opacity must not exceed 20% during the acceleration mode, 15% during the lugging mode and 50% during peaks in either mode
  All the above is verified by the manufacturing testing
  Purchase a compliant engine
  Emission standards applicability will depend on the generator size, manufacturing year, and displacement.

## Slide 14: NSPS and Emergency Generators Cont.
Fuel Requirements - Currently available low sulfur non-road (red dye) diesel
  Use the currently available ultra low sulfur on-road diesel (available at gas stations)
  All the delayed compliance dates have passed
Importing /Installation Requirements – most of the delayed dates have passed
  Does not apply to engines that were removed from one location and reinstalled at a new location

## Slide 15: NSPS and Emergency Generators Cont.
Monitoring Requirements:
  Install a non-resettable hour meter
  If the engine has a diesel particulate filter to comply with the applicable emission standard install a backpressure monitor that alarms when the backpressure limit is approached
Compliance Requirements:
  Operate and maintain the engine to achieve the emission standards over the entire life of the engine
  Operate and maintain the engine (and control device) according to the manufacturer’s instructions
  Purchase a certified engine

## Slide 16: NSPS and Emergency Generators Cont.
Compliance Requirements (continued):
  No operational limit in emergency situations
  100 hours per calendar year limit for:
    Maintenance checks and readiness testing
    Emergency demand response (needs to be specifically addressed in your air quality permit)
    Periods where there is a deviation of voltage or frequency of 5% or greater below standard voltage or frequency
  50 hours per calendar year limit for non-emergency use
    Counts toward the 100 hour limit above
    Cannot be used for peak shaving or non-emergency demand response or to supply power to the grid (possible under certain conditions)

## Slide 17: NSPS and Emergency Generators Cont.
Compliance Requirements (continued):
  Failure to follow the manufacturer’s instructions will result in:
    Developing a maintenance plan and
    Conducting performance testing (reoccurring if over 500 HP)
Testing Requirements:
  No requirements
  Violation of any applicable standard requires testing per 40 CFR 60.4212

## Slide 18: NSPS and Emergency Generators Cont.
Notification, Reports, and Records Requirements:
  No Federal initial notification required
    Check with your local Air Quality permitting agency to see if you need a permit.
  If equipped with a particulate matter filter keep records of corrective actions in response to the backpressure monitor alarms
  If greater than 100 HP and operates (or contractually obligated to be available) for more than 15 hours per calendar year for emergency demand response see 40 CFR 60.4214(d) for report requirements (includes electronic reporting to the USEPA)

## Slide 19: NSPS and Non-Emergency Generators
Example: 450 HP Compression Ignition (or CI or diesel) Non-Emergency Generator, Manufactured 5/1/2015
Engines subject to an NSPS comply with the NESHAP by complying with the NSPS
NSPS Subpart IIII = Diesel

## Slide 20: NSPS and Non-Emergency Generators Cont.
Similar to Emergency Generators with the following exceptions
Emission Standards – must comply with the current Tier based on the year of manufacture
  i.e., Tier 4 after 2014 model year
The emergency hourly limits do not apply
  Air Quality permit will likely set an annual operational limit
Generally non-emergency engines located at a facility for more than one year will need an air quality permit.
  Replacements do not reset the clock

## Slide 21: Contact Information
Anu Jain
Pinal County Air Quality
520-866-6931
anu.Jain@pinalcountyaz.gov